## EARTHING
S/N | PAGE | CABLE CSA mm2 | ITEM | DESCRIPTION
1 | 1 | 50 | 6.A | Transformer Cubicle
2 | 1 | 50 | 7.A | Rectifier
3 | 1 | 50 | 85.B | Storage Bottles
4 | 1 | 51 | 85.A | Storage Bottles
5 | 1 | 70 | 9.A | Electrolyser 1 System Skid
6 | 1 | 70 |  | Electrolyser 1 System H2/Lye Seperator
7 | 1 | 70 | 9.A | Electrolyser 1 System Fore Electrodes
8 | 1 | 50 | 64.A | Dryer H2
9 | 1 | 50 |  | Control Cubicle
10 | 1 | 25 |  | EXI - Compartment Insulated IS/PC Earth Bar
11 | 1 | 50 | 14 | Scrubber
12 | 1 | 50 | 3.B | Water Purifier System
13 | 1 | 50 | 64.B | Dryer H2
14 | 1 | 70 | 9.B | Electrolyser 2 System Fore Electrodes
15 | 1 | 70 |  | Electrolyser 2 System H2/Lye Seperator
16 | 1 | 70 | 9.B | Electrolyser 2 System Skid
17 | 1 | 50 | 36 | Lye Tank
18 | 1 | 50 | 60 | Deoxydiser
19 | 1 | 50 | 7.B | Rectifier
20 | 1 | 50 | 6.B | Transformer Cubicle
21 | 1 | 50 | 81.A | H2 High Pressure Compressor Skid
22 | 1 | 50 | 81.B | H2 High Pressure Compressor Skid
23 | 1 | 50 | 13 | H2 Gas Holder
24 | 1 | 50 |  | Cable Tray
25 | 1 | 50 |  | Cable Tray

## TERMINAL CABLES
S/N | PAGE | TERMINAL | CONTACT | WIRE | CABLE | CONNECTION | POLARITY | PROCESS | TAG | DESCRIPTION
1 | 2 | X20 | 1 | 1 | W1 | 1 | NC | Alarm | Cable | Customer Rec. 1/2 To Zero
2 | 2 | X20 | 2 | 2 | W1 | 2 | C |  | Cable
3 | 2 | X20 | 3 | 1 | W2 | 1 | NC | Alarm | Cable | Fire Detection Trip
4 | 2 | X20 | 4 | 2 | W2 | 2 | C |  | Cable
5 | 2 | X20 | 5 | 1 | W3 | 1 | NC | Compressor A | Cable | HS 81A.1 Emerbency Switch Compressor A
6 | 2 | X20 | 6 | 2 | W3 | 2 | C |  | Cable
7 | 2 | X20 | 7 | 1 | W4 | 1 | NC | Emergency Switch | Cable | HS 1.2A Emergency Switch
8 | 2 | X20 | 8 | 2 | W4 | 2 | C |  | Cable
9 | 2 | X20 | 9 | 1 | W5 | 1 | NC | Emergency Switch | Cable | HS 1.2B Emergency Switch
10 | 2 | X20 | 10 | 2 | W5 | 2 | C |  | Cable
11 | 2 | X20 | 11 | 1 | W6 | 1 | NC | Emergency Switch | Cable | HS 1.2C Emergency Switch
12 | 2 | X20 | 12 | 2 | W6 | 2 | C |  | Cable
13 | 2 | X20 | 13 | 1 | W7 | 1 | + | Rectifier A | Cable | Rectifier A Voltage Output
14 | 2 | X20 | 14 | 2 | W7 | 2 | - |  | Cable
15 | 2 | X20 | 15 | 3 | W7 | 3 | + | Rectifier A | Cable | Rectifier A Current Output
16 | 2 | X20 | 16 | 4 | W7 | 4 | - |  | Cable
17 | 2 | X20 | 17 | 1 | W8 | 1 | + | Rectifier A | Cable | Rectifier A Control
18 | 2 | X20 | 18 | 2 | W8 | 2 | - |  | Cable
19 | 2 | X20 | 19 | 1 | W9 | 1 | NC | Rectifier A | Cable | Rectifier A Common Alarm
20 | 2 | X20 | 20 | 2 | W9 | 2 | C |  | Cable
21 | 2 | X20 | 21 | 3 | W9 | 3 | NC | Rectifier A | Cable | Rectifier A Running
22 | 2 | X20 | 22 | 4 | W9 | 4 | C |  | Cable
23 | 2 | X20 | 23 | 5 | W9 | 5 |  | Rectifier A | Cable | Rectifier A Run/Block
24 | 2 | X20 | 24 | 6 | W9 | 6 |  |  | Cable
25 | 2 | X20 | 25 | 7 | W9 | 7 |  | Rectifier A | Cable | Rectifier A Reset
26 | 2 | X20 | 26 | 8 | W9 | 8 |  |  | Cable
27 | 3 | X20 | 27 | 1 | W10 | 1 | 23 | Compressor B | Cable | Start/Stop HS 81B.1 Compressor B
28 | 3 | X20 | 28 | 2 | W10 | 2 | 24 |  | Cable
29 | 3 | X20 | 29 | 3 | W10 | 3 | 11 |  | Cable
30 | 3 | X20 | 30 | 1 | W11 | 1 | 23 | Lye Pump AA | Cable | Start/Stop HS 30.AA Lye Circulation Pump AA
31 | 3 | X20 | 31 | 2 | W11 | 2 | 24 |  | Cable
32 | 3 | X20 | 32 | 3 | W11 | 3 | 11 |  | Cable
33 | 3 | X20 | 33 | 1 | W12 | 1 | 23 | Scrubber | Cable | Start/Stop HS 15.1 Scrubber Pump
34 | 3 | X20 | 34 | 2 | W12 | 2 | 24 |  | Cable
35 | 3 | X20 | 35 | 3 | W12 | 3 | 11 |  | Cable
36 | 3 | X20 | 36 | 1 | W13 | 1 | 23 | Compressor A | Cable | Start/Stop HS 81A.1 H2 Compressor A
37 | 3 | X20 | 37 | 2 | W13 | 2 | 24 |  | Cable
38 | 3 | X20 | 38 | 3 | W13 | 3 | 11 |  | Cable
39 | 3 | X20 | 39 | Spare |  |  |  |  | Cable
40 | 3 | X20 | 40 | Spare |  |  |  |  | Cable
41 | 3 | X20 | 41 | 1 | W14 | 1 | + | Rectifier B | Cable | Rectifier B Voltage Output
42 | 3 | X20 | 42 | 2 | W14 | 2 | - |  | Cable
43 | 3 | X20 | 43 | 1 | W15 | 1 | + | Rectifier B | Cable | Rectifier B Current Output
44 | 3 | X20 | 44 | 2 | W15 | 2 | - |  | Cable
45 | 3 | X20 | 45 | 1 | W16 | 1 | + | Rectifier B | Cable | Rectifier B Control
46 | 3 | X20 | 46 | 2 | W16 | 2 | - |  | Cable
47 | 3 | X20 | 47 | 1 | W17 | 1 |  | Rectifier B | Cable | Rectifier B Common Alarm
48 | 3 | X20 | 48 | 2 | W17 | 2 |  |  | Cable
49 | 3 | X20 | 49 | 3 | W17 | 3 |  | Rectifier B | Cable | Rectifier B Running
50 | 3 | X20 | 50 | 4 | W17 | 4 |  |  | Cable
51 | 3 | X20 | 51 | 5 | W17 | 5 |  | Rectifier B | Cable | Rectifier B Run/Block
52 | 3 | X20 | 52 | 6 | W17 | 6 |  |  | Cable
53 | 3 | X20 | 53 | 7 | W17 | 7 |  | Rectifier B | Cable | Rectifier B Reset
54 | 3 | X20 | 54 | 8 | W17 | 8 |  |  | Cable
55 | 4 | X20 | 55 | 1 | W18 | 1 | NC | Alarm | Cable | Customer Rec. 1/2 To Zero
56 | 4 | X20 | 56 | 2 | W18 | 2 | C |  | Cable
57 | 4 | X20 | 57 | 1 | W19 | 1 | NC | Customer Trip | Cable | Customer Trip
58 | 4 | X20 | 58 | 2 | W19 | 2 | C |  | Cable
59 | 4 | X20 | 59 | 1 | W20 | 1 | NC | Alarm | Cable | Common Yellow Alarm
60 | 4 | X20 | 60 | 2 | W20 | 2 | C |  | Cable
61 | 4 | X20 | 61 | 1 | W21 | 1 | NC | Alarm | Cable | Common Red Alarm
62 | 4 | X20 | 62 | 2 | W21 | 2 | C |  | Cable
63 | 4 | X20 | 63 | 1 | W22 | 1 | 23 | Lye Pump AB | Cable | Start/Stop HS 30AB Lye Circulation Pump AB
64 | 4 | X20 | 64 | 2 | W22 | 2 | 24 |  | Cable
65 | 4 | X20 | 65 | 3 | W22 | 3 | 11 |  | Cable
66 | 4 | X20 | 66 | 1 | W23 | 1 | 23 | Lye Pump BA | Cable | Start/Stop HS 30BA Lye Circulation Pump BA
67 | 4 | X20 | 67 | 2 | W23 | 2 | 24 |  | Cable
68 | 4 | X20 | 68 | 3 | W23 | 3 | 11 |  | Cable
69 | 4 | X20 | 69 | 1 | W24 | 1 | 23 | Lye Pump BB | Cable | Start/Stop HS 30BB Lye Circulation Pump BB
70 | 4 | X20 | 70 | 2 | W24 | 2 | 24 |  | Cable
71 | 4 | X20 | 71 | 3 | W24 | 3 | 11 |  | Cable
72 | 4 | X20 | 72 | 1 | W25 | 1 | 23 | Scrubber | Cable | Start/Stop HS 15B Scrubber Pump B
73 | 4 | X20 | 73 | 2 | W25 | 2 | 24 |  | Cable
74 | 4 | X20 | 74 | 3 | W25 | 3 | 11 |  | Cable
75 | 4 | X20 | 75 | 1 | W26 | 1 | 1 | H2 In Air Sensor 1 | Cable | H2 In Air Sensor 1
76 | 4 | X20 | 76 | 2 | W26 | 2 | 2 |  | Cable
77 | 4 | X20 | 77 | 3 | W26 | 3 | 3 |  | Cable
78 | 4 | X20 | 78 | 4 | W26 | 4 | 4 |  | Cable
79 | 5 | X20 | 79 | 1 | W27 | 1 | 1 | H2 In Air Sensor 2 | Cable | H2 In Air Sensor 2
80 | 5 | X20 | 80 | 2 | W27 | 2 | 2 |  | Cable
81 | 5 | X20 | 81 | 3 | W27 | 3 | 3 |  | Cable
82 | 5 | X20 | 82 | 4 | W27 | 4 | 4 |  | Cable
83 | 5 | X20 | 83 | 1 | W28 | 1 | 1 | H2 In Air Sensor 3 | Cable | H2 In Air Sensor 3
84 | 5 | X20 | 84 | 2 | W28 | 2 | 2 |  | Cable
85 | 5 | X20 | 85 | 3 | W28 | 3 | 3 |  | Cable
86 | 5 | X20 | 86 | 4 | W28 | 4 | 4 |  | Cable
87 | 5 | X20 | 87 | 1 | W29 | 1 | 1 | H2 In Air Sensor 4 | Cable | H2 In Air Sensor 4
88 | 5 | X20 | 88 | 2 | W29 | 2 | 2 |  | Cable
89 | 5 | X20 | 89 | 3 | W29 | 3 | 3 |  | Cable
90 | 5 | X20 | 90 | 4 | W29 | 4 | 4 |  | Cable
91 | 5 | X20 | 91 | 1 | W30 | 1 | NC | Compressor B | Cable | HS 81B.1 Emergency Switch Compressor B
92 | 5 | X20 | 92 | 2 | W30 | 2 | C |  | Cable
93 | 5 | X20 | 93 | 1 |  | 1 | 1 | Alarm | Cable | Field Water Purification Plant High Level Alarm And Pump Fault
94 | 5 | X20 | 94 | 2 |  | 2 | 2 |  | Cable
95 | 5 | X20 | 95 | 3 |  | 3 | 3 |  | Cable
96 | 6 | X30 | 1 | 1 | W31 | 1 | U | Lye Pump AA | Cable | K30AA Lye Circulation Pump 30AA
97 | 6 | X30 | 2 | 2 | W31 | 2 | Y |  | Cable
98 | 6 | X30 | 3 | 3 | W31 | 3 | W |  | Cable
99 | 6 | X30 | 4 | 1 | W32 | 1 | U | Scrubber | Cable | K15 Scrubber Pump
100 | 6 | X30 | 5 | 2 | W32 | 2 | Y |  | Cable
101 | 6 | X30 | 6 | 3 | W32 | 3 | W |  | Cable
102 | 6 | X30 | 7 | 1 | W33 | 1 | 6 | Rectifier A | Cable | Main Supply Rectifyer Vent Fan A
103 | 6 | X30 | 8 | 2 | W33 | 2 | 4 |  | Cable
104 | 6 | X30 | 9 | 3 | W33 | 3 | 2 |  | Cable
105 | 6 | X30 | 10 | 1 | W34 | 1 | 6 | Rectifier B | Cable | Main Supply Rectifyer Vent Fan B
106 | 6 | X30 | 11 | 2 | W34 | 2 | 4 |  | Cable
107 | 6 | X30 | 12 | 3 | W34 | 3 | 2 |  | Cable
108 | 6 | X31 | 1 | 1 | W35 | 1 | U | Compressor A | Cable | M81A Compressor A
109 | 6 | X31 | 2 | 2 | W35 | 2 | Y |  | Cable
110 | 6 | X31 | 3 | 3 | W35 | 3 | W |  | Cable
111 | 6 | X31 | 4 | 1 | W36 | 1 | U | Compressor B | Cable | M81B Compressor B
112 | 6 | X31 | 5 | 2 | W36 | 2 | Y |  | Cable
113 | 6 | X31 | 6 | 3 | W36 | 3 | W |  | Cable
114 | 7 | X30 | 13 | 1 | W37 | 1 | U | Lye Pump AB | Cable | K30AB Lye Circulation 30AB
115 | 7 | X30 | 14 | 2 | W37 | 2 | Y |  | Cable
116 | 7 | X30 | 15 | 3 | W37 | 3 | W |  | Cable
117 | 7 | X30 | 16 | 1 | W38 | 1 | U | Lye Pump BA | Cable | K30BA Lye Circulation 30BA
118 | 7 | X30 | 17 | 2 | W38 | 2 | Y |  | Cable
119 | 7 | X30 | 18 | 3 | W38 | 3 | W |  | Cable
120 | 7 | X30 | 19 | 1 | W39 | 1 | U | Lye Pump BB | Cable | K30BB Lye Circulation 30BB
121 | 7 | X30 | 20 | 2 | W39 | 2 | Y |  | Cable
122 | 7 | X30 | 21 | 3 | W39 | 3 | W |  | Cable
123 | 7 | X30 | 22 | 1 | W40 | 1 | U | Scrubber | Cable | K15B Scrubber Pump B
124 | 7 | X30 | 23 | 2 | W40 | 2 | Y |  | Cable
125 | 7 | X30 | 24 | 3 | W40 | 3 | W |  | Cable
126 | 8 | X1 | 1 | 1 | W41 | 1 | + | Electrolyser B | Cable | Feed Water Supply Lye System (Valve FW-111B-2) Electrolyser B
127 | 8 | X1 | 2 | 2 | W41 | 2 | - |  | Cable
128 | 8 | X1 | 3 | 1 | W42 | 1 | + | Scrubber | Cable | Feed Water Supply Scrubber (Valve FW-121-2)
129 | 8 | X1 | 4 | 2 | W42 | 2 | - |  | Cable
130 | 8 | X1 | 5 | 1 | W43 | 1 | + | Electrolyser A | Cable | Feed Water Supply Lye System (Valve FW-111A-2) Electrolyser A
131 | 8 | X1 | 6 | 2 | W43 | 2 | - |  | Cable
132 | 8 | X1 | 7 | 1 | W44 | 1 | 1 | Compressor A | Cable | Draining 1st Stage Compressor 81A Valve 81A-V13
133 | 8 | X1 | 8 | 2 | W44 | 2 | N |  | Cable
134 | 8 | X1 | 9 | 3 | W44 | 3 | 2 | Compressor A | Cable | Draining 2nd Stage Compressor 81A Valve 81A-V14
135 | 8 | X1 | 10 | 4 | W44 | 4 | N |  | Cable
136 | 8 | X1 | 11 | 5 | W44 | 5 | 3 | Compressor A | Cable | Draining 3rd Stage Compressor 81A Valve 81A-V15
137 | 8 | X1 | 12 | 6 | W44 | 6 | N |  | Cable
138 | 8 | X1 | 13 | 7 | W44 | 7 | 4 | Compressor A | Cable | Draining 4th Stage Compressor 81A Valve 81A-V16
139 | 8 | X1 | 14 | 8 | W44 | 8 | N |  | Cable
140 | 8 | X1 | 15 | 9 | W44 | 9 | 5 | Compressor A | Cable | Draining After Filter Compressor 81A Valve 81A-V41
141 | 8 | X1 | 16 | 10 | W44 | 10 | N |  | Cable
142 | 8 | X1 | 17 | 11 | W44 | 11 | 6 | Compressor A | Cable | Draining Condensate Pot Compressor 81A Valve 81A-V31
143 | 8 | X1 | 18 | 12 | W44 | 12 | N |  | Cable
144 | 8 | X1 | 19 | 9 | W45 | 9 | 7 | Dryer A | Cable | Repressurisation Control Valve Dryer 64A Valve 64A-V16
145 | 8 | X1 | 20 | 10 | W45 | 10 | N |  | Cable
146 | 8 | X1 | 21 | 11 | W45 | 11 | 8 | Dryer A | Cable | Drain Dryer 64A Valve 64A-V7
147 | 8 | X1 | 22 | 12 | W45 | 12 | N |  | Cable
148 | 8 | X1 | 23 | 1 | W45 | 1 | 2 | Dryer A | Cable | Tower A In Operaton Dryer 64A Valve 64A-V3
149 | 8 | X1 | 24 | 2 | W45 | 2 | N |  | Cable
150 | 8 | X1 | 25 | 3 | W45 | 3 | 3 | Dryer A | Cable | Tower B In Operaton Dryer 64A Valve 64A-V4
151 | 8 | X1 | 26 | 2 | W45 |  | N |  | Cable
152 | 9 | X1 | 27 | 4 | W45 | 1 | 4 | Dryer A | Cable | Depressurisation Valve Tower A Dryer 64A (64A-V7)
153 | 9 | X1 | 28 | 5 | W45 | 2 | N |  | Cable
154 | 9 | X1 | 29 | 6 | W45 | 3 | 5 | Dryer A | Cable | Depressurisation Valve Tower B Dryer 64A (64A-V8)
155 | 9 | X1 | 30 | 7 | W45 | 4 | N |  | Cable
156 | 9 | X1 | 31 | 8 | W45 | 5 | 6 | Dryer A | Cable | Control Valve Regeneration Dryer 64A (64A-V12)
157 | 9 | X1 | 32 | 7 | W45 | 6 | N |  | Cable
158 | 9 | X1 | 33 | 1 | W47 | 1 | 1 | Compressor B | Cable | Draining 1st Stage Compressor 81B Valve 81B-V13
159 | 9 | X1 | 34 | 2 | W47 | 2 | N |  | Cable
160 | 9 | X1 | 35 | 3 | W47 | 3 | 2 | Compressor B | Cable | Draining 2nd Stage Compressor 81B Valve 81B-V14
161 | 9 | X1 | 36 | 4 | W47 | 4 | N |  | Cable
162 | 9 | X1 | 37 | 5 | W47 | 5 | 3 | Compressor B | Cable | Draining 3rd Stage Compressor 81B Valve 81B-V15
163 | 9 | X1 | 38 | 6 | W47 | 6 | N |  | Cable
164 | 9 | X1 | 39 | 7 | W47 | 7 | 4 | Compressor B | Cable | Draining 4th Stage Compressor 81B Valve 81B-V16
165 | 9 | X1 | 40 | 8 | W47 | 8 | N |  | Cable
166 | 9 | X1 | 41 | 9 | W47 | 9 | 5 | Compressor B | Cable | Draining After Filter Compressor 81B Valve 81B-V41
167 | 9 | X1 | 42 | 10 | W47 | 10 | N |  | Cable
168 | 9 | X1 | 43 | 11 | W47 | 11 | 6 | Compressor B | Cable | Draining Condensate Pot Compressor 81B Valve 81B-V31
169 | 9 | X1 | 44 | 12 | W47 | 12 | N |  | Cable
170 | 9 | X1 | 45 | 9 | W48 | 9 | 7 | Dryer B | Cable | Repressurisation Control Valve Dryer 64B Valve 64B-V16
171 | 9 | X1 | 46 | 10 | W48 | 10 | N |  | Cable
172 | 9 | X1 | 47 | 11 | W48 | 11 | 8 | Dryer B | Cable | Drain Dryer 64B Valve 64B-V7
173 | 9 | X1 | 48 | 12 | W48 | 12 | N |  | Cable
174 | 9 | X1 | 49 | 1 | W48 | 1 | 2 | Dryer B | Cable | Tower A In Operaton Dryer 64B Valve 64B-V3
175 | 9 | X1 | 50 | 2 | W48 | 2 | N |  | Cable
176 | 9 | X1 | 51 | 3 | W48 | 3 | 3 | Dryer B | Cable | Tower B In Operaton Dryer 64B Valve 64B-V4
177 | 9 | X1 | 52 | 2 | W48 |  | N |  | Cable
178 | 10 | X1 | 53 | 4 | W48 | 4 | 4 | Dryer B | Cable | Depressurisation Valve Tower A Dryer 64B (64B-V7)
179 | 10 | X1 | 54 | 5 | W48 | 5 | N |  | Cable
180 | 10 | X1 | 55 | 6 | W48 | 6 | 5 | Dryer B | Cable | Depressurisation Valve Tower B Dryer 64B (64B-V8)
181 | 10 | X1 | 56 | 7 | W48 | 7 | N |  | Cable
182 | 10 | X1 | 57 | 8 | W48 | 8 | 6 | Dryer B | Cable | Control Valve Regeneration Dryer 64B (64B-V12)
183 | 10 | X1 | 58 | 7 | W48 |  | N |  | Cable
184 | 11 | X25 | 1 | [5 empty] | Cable
185 | 11 | X25 | 2 | [5 empty] | Cable
186 | 11 | X25 | 3 | 3 | W51 | 2 | Phase | Deoxydiser | Cable | Deoxydiser 60 Preheater Element Temperature HH
187 | 11 | X25 | 4 | [5 empty] | Cable
188 | 11 | X25 | 5 | 1 | W51 | 1 | Phase |  | Cable
189 | 11 | X25 | 6 | 2 | W51 | 2 | Phase |  | Cable
190 | 11 | X25 | 7 | 1 | W52 | 1 | Phase | Dryer A | Cable | Dryer 64A Heater
191 | 11 | X25 | 8 | 2 | W52 | 2 | Phase |  | Cable
192 | 11 | X25 | 9 | 1 | W53 | 1 | Phase | Dryer B | Cable | Dryer 64B Heater
193 | 11 | X25 | 10 | 2 | W53 | 2 | Phase |  | Cable
194 | 12 | X12 | 1 | 1 | W54 | 1 | NO | Cooling Water | Cable | Pressure Switch PS-101.1 K153 Pressure Low Cooling Water Inlet
195 | 12 | X12 | 2 | 2 | W54 | 2 | C |  | Cable
196 | 12 | X12 | 3 | 1 | W55 | 1 | NO | Instrument Air | Cable | Pressure Switch PS-101.2 K154 Pressure Instrument Air Inlet
197 | 12 | X12 | 4 | 2 | W55 | 2 | C |  | Cable
198 | 12 | X12 | 5 | 1 | W56 | 1 | NO |  | Cable | Pressure Switch PS-101.3 K155 Pressure Inlet H2 Low
199 | 12 | X12 | 6 | 2 | W56 | 2 | C |  | Cable
200 | 12 | X12 | 7 | 5 | W57 | 5 | 19 | Compressor A | Cable | Pressure Transmitter PT-81A K122 Inlet Suction Pressure Low Compressor 81A
201 | 12 | X12 | 8 | 6 | W57 | 6 | 20 |  | Cable
202 | 12 | X12 | 9 | 1 | W57 | 1 | 5 | Compressor A | Cable | Pressure Switch PS-81A.20 K128 Pressure High Condensate Tank Compressor 81A
203 | 12 | X12 | 10 | 2 | W57 | 2 | 6 |  | Cable
204 | 12 | X12 | 11 | 3 | W57 | 3 | 3 | Compressor A | Cable | Pressure Switch PS-81A.12 K127 Discharge Pressure High Compressor 81A
205 | 12 | X12 | 12 | 4 | W57 | 4 | 4 |  | Cable
206 | 12 | X12 | 13 | [5 empty] | Cable
207 | 12 | X12 | 14 | [5 empty] | Cable
208 | 12 | X12 | 15 | Spare |  |  |  |  | Cable
209 | 12 | X12 | 16 | Spare |  |  |  |  | Cable
210 | 12 | X12 | 17 | Spare |  |  |  |  | Cable
211 | 12 | X12 | 18 | Spare |  |  |  |  | Cable
212 | 12 | X12 | 19 | 1 | W60 | 1 | NO | Deoxydiser | Cable | Temperature Hgh TSHH-60.3 Preheater Temperature High Deoxydiser
213 | 12 | X12 | 20 | 2 | W60 | 2 | C |  | Cable
214 | 12 | X12 | 21 | 3 | W60 | 3 | NO | Deoxydiser | Cable | Temperature Switch TSH-61.7 Outlet Temperature High High Deoxydiser
215 | 12 | X12 | 22 | 4 | W60 | 4 | C |  | Cable
216 | 12 | X12 | 23 | 1 | W89 | 1 | NO | Electrolyser B | Cable | Level Switch LST-208.2 Level Low Low Electrolyser B
217 | 12 | X12 | 24 | 2 | W89 | 2 | C |  | Cable
218 | 12 | X12 | 25 | 1 | W62 | 1 | NO | Electrolyser B | Cable | Flow Switch FIS-30B.2 Lye Circulation Low Electrolyser B
219 | 12 | X12 | 26 | 2 | W62 | 2 | C |  | Cable
220 | 12 | X12 | 27 | 1 | W46 | 1 | NO | Dryer B | Cable | Flow Switch FBL-64B.5 Level Low Dryer 64B
221 | 12 | X12 | 28 | 2 | W46 | 2 | C |  | Cable
222 | 13 | X12 | 29 | 11 | W46 | 11 | 17 | Dryer A | Cable | Flow Switch FSL-64A5 Level Low Dryer 64A
223 | 13 | X12 | 30 | 12 | W46 | 12 | 18 |  | Cable
224 | 13 | X12 | 31 | 1 | W65 | 1 | NO | Electrolyser B | Cable | Temperature Switch TIS-108.2 Lye Temperature Electrolyser B Gas/Lye Separator
225 | 13 | X12 | 32 | 2 | W65 | 2 | C |  | Cable
226 | 13 | X12 | 33 | 1 | W88 | 3 | NO |  | Cable | Level Switch LST-20A.2 Level Low Low O2 Gas/Lye Separator
227 | 13 | X12 | 34 | 2 | W88 | 4 | C |  | Cable
228 | 13 | X12 | 35 | 1 | W67 | 1 | NO | Scrubber | Cable | Level Switch LSLL-14.2 Level Low Low Feed Water Scrubber
229 | 13 | X12 | 36 | 2 | W67 | 2 | C |  | Cable
230 | 13 | X12 | 37 | 3 | W67 | 3 | NO | Scrubber | Cable | Level Switch LSL-14.2 Level Low Feed Water Scrubber Item 14
231 | 13 | X12 | 38 | 4 | W67 | 4 | C |  | Cable
232 | 13 | X12 | 39 | 5 | W67 | 5 | NC | Scrubber | Cable | Level Switch LSH-14.2 Level High Feed Water Scrubber Item 14
233 | 13 | X12 | 40 | 6 | W67 | 6 | C |  | Cable
234 | 13 | X12 | 41 | 1 | W70 | 1 | 1 | Compressor A | Cable | Temperature Switch TSH-81A.13 Discharge Temperature High Pressure Compressor A
235 | 13 | X12 | 42 | 2 | W70 | 2 | 2 |  | Cable
236 | 13 | X12 | 43 | 3 | W70 | 3 | 16 | Compressor A | Cable | Level Switch LSLL-81A.14 Condensate Level Low Low HP Compressor A
237 | 13 | X12 | 44 | 4 | W70 | 4 | 17 |  | Cable
238 | 13 | X12 | 45 | 5 | W70 | 5 | 13 | Compressor A | Cable | Level Switch LSL-81A.15 Condensate Level Low HP Compressor A
239 | 13 | X12 | 46 | 6 | W70 | 6 | 14 |  | Cable
240 | 13 | X12 | 47 | 7 | W70 | 7 | 10 | Compressor A | Cable | Level Switch LSH-81A.16 Condensate Level High HP Compressor A
241 | 13 | X12 | 48 | 8 | W70 | 8 | 11 |  | Cable
242 | 13 | X12 | 49 | 9 | W70 | 9 | 7 | Compressor A | Cable | Level Switch LSHH-81A.17 Condensate Level High High HP Compressor A
243 | 13 | X12 | 50 | 10 | W70 | 10 | 8 |  | Cable
244 | 13 | X12 | 51 | 1 | W49 | 7 | 2 | Dryer B | Cable | Temperature Switch TSH-64B.6 Heater Temperature Dryer 64B
245 | 13 | X12 | 52 | 2 | W49 | 8 | 3 |  | Cable
246 | 13 | X12 | 53 | 1 | W72 | 1 | NO | Gas Holder | Cable | Level Switch LSL-13.2 Level Low Gas Holder
247 | 13 | X12 | 54 | 2 | W72 | 2 | C |  | Cable
248 | 13 | X12 | 55 | 1 | W73 | 1 | NO | Electrolyser A | Cable | Flow Switch FISL-30A.2 Lye Circulation Low Electrolyser A
249 | 13 | X12 | 56 | 2 | W73 | 2 | C |  | Cable
250 | 14 | X12 | 57 | 1 | W74 | 1 | NC | Electrolyser A | Cable | Temperature Switch TS-10A.2 Lye Temperature Electrolyser A Gas/Lye Separator
251 | 14 | X12 | 58 | 2 | W74 | 2 | C |  | Cable
252 | 14 | X12 | 59 | 1 | W46 | 1 | 1 | Dryer A | Cable | Temperature S+I253:I266witch TS-64A.6 Heater Temperature Dryer 64A
253 | 14 | X12 | 60 | 2 | W46 | 2 | 2 |  | Cable
254 | 14 | X12 | 61 | 9 | W46 | 9 | 15 | Dryer A | Cable | Pressure Switch PSH-64A.2 Outlet Pressure Tower B Dryer 64A
255 | 14 | X12 | 62 | 10 | W46 | 10 | 16 |  | Cable
256 | 14 | X12 | 63 | 7 | W46 | 7 | 12 | Dryer A | Cable | Pressure Switch PSL-64A.2 Outlet Pressure Tower B Dryer 64A
257 | 14 | X12 | 64 | 8 | W46 | 8 | 13 |  | Cable
258 | 14 | X12 | 65 | 3 | W49 | 3 | 7 | Dryer B | Cable | Pressure Switch PSL-64B.1 Outlet Pressure Tower A Dryer 64B
259 | 14 | X12 | 66 | 4 | W49 | 4 | 8 |  | Cable
260 | 14 | X12 | 67 | 5 | W49 | 5 | 10 | Dryer B | Cable | Pressure Switch PSH-64B.1 Outlet Pressure Tower A Dryer 64B
261 | 14 | X12 | 68 | 6 | W49 | 6 | 11 |  | Cable
262 | 14 | X12 | 69 | 7 | W49 | 7 | 12 | Dryer B | Cable | Pressure Switch PSL-64B.2 Outlet Pressure Tower B Dryer 64B
263 | 14 | X12 | 70 | 8 | W49 | 8 | 13 |  | Cable
264 | 14 | X12 | 71 | 9 | W49 | 9 | 15 | Dryer B | Cable | Pressure Switch PSH-64B.2 Outlet Pressure Tower B Dryer 64B
265 | 14 | X12 | 72 | 10 | W49 | 10 | 16 |  | Cable
266 | 14 | X12 | 73 | 5 | W82 | 5 | 19 | Compressor B | Cable | Pressure Transmitter PT-81B.1 Inlet Suction Pressure Compressor 81B
267 | 14 | X12 | 74 | 6 | W82 | 6 | 20 |  | Cable
268 | 14 | X12 | 75 | 3 | W82 | 3 | 5 | Compressor B | Cable | Pressure Switch PSH-81B.20 Pressure Condensate Tank Compressor 81B
269 | 14 | X12 | 76 | 4 | W82 | 4 | 6 |  | Cable
270 | 14 | X12 | 77 | 1 | W82 | 1 | 3 | Compressor B | Cable | Pressure Switch PSH-81B.12 Discharge Pressure Compressor 81B
271 | 14 | X12 | 78 | 2 | W82 | 2 | 4 |  | Cable
272 | 14 | X12 | 79 | [5 empty] | Cable
273 | 14 | X12 | 80 | [5 empty] | Cable
274 | 14 | X12 | 81 | 9 | W83 | 9 | 1 | Compressor B | Cable | Temperature Switch TSH-81B.13 Discharge Temperature Compressor 81B
275 | 14 | X12 | 82 | 10 | W83 | 10 | 2 |  | Cable
276 | 14 | X12 | 83 | 3 | W83 | 3 | 16 | Compressor B | Cable | Level Switch LSLL-81B.14 Condensate Level Low Low HP Compressor 81B
277 | 14 | X12 | 84 | 4 | W83 | 4 | 18 |  | Cable
278 | 15 | X12 | 85 | 8 | W83 | 8 | 14 | Compressor B | Cable | Level Switch LSL-81B.15 Condensate Level Low HP Compressor 81B
279 | 15 | X12 | 86 | 9 | W83 | 9 | 15 |  | Cable
280 | 15 | X12 | 87 | 6 | W83 | 6 | 11 | Compressor B | Cable | Level Switch LSH-81B.16 Condensate Level High HP Compressor 81B
281 | 15 | X12 | 88 | 7 | W83 | 7 | 12 |  | Cable
282 | 15 | X12 | 89 | 5 | W83 | 5 | 8 | Compressor B | Cable | Level Switch LSHH-81B.17 Condensate Level High High HP Compressor 81B
283 | 15 | X12 | 90 | 6 | W83 | 6 | 9 |  | Cable
284 | 15 | X12 | 91 | Spare |  |  |  |  | Cable
285 | 15 | X12 | 92 | Spare |  |  |  |  | Cable
286 | 15 | X12 | 93 | 3 | W46 | 3 | 7 | Dryer A | Cable | Pressure Switch PSL-64A.1 Outlet Pressure Tower A Dryer 64A
287 | 15 | X12 | 94 | 4 | W46 | 4 | 8 |  | Cable
288 | 15 | X12 | 95 | 5 | W46 | 5 | 9 | Dryer A | Cable | Pressure Switch PSH-64A.1 Outlet Pressure Tower A Dryer 64A
289 | 15 | X12 | 96 | 6 | W46 | 6 | 10 |  | Cable
290 | 15 | X12 | 97 | 1 | W86 | 1 | + | Gas Holder | Cable | LT-13.1 Level Gas Holder
291 | 15 | X12 | 98 | 2 | W86 | 2 | - |  | Cable
292 | 15 | X12 | 99 | 1 | W87 | 1 | + | Pressure Bottles | Cable | PT-85.2 H2 Pressure Bottles
293 | 15 | X12 | 100 | 2 | W87 | 2 | - |  | Cable
294 | 15 | X12 | 101 | Spare |  |  |  |  | Cable
295 | 15 | X12 | 102 | Spare |  |  |  |  | Cable
296 | 15 | X12 | 103 | Spare |  |  |  |  | Cable
297 | 15 | X12 | 104 | Spare |  |  |  |  | Cable
298 | 15 | X12 | 105 | 1 | W88 | 1 | + |  | Cable | LST-20A.2 Lye Level Fas/Lye Separator 20A
299 | 15 | X12 | 106 | 2 | W88 | 2 | - |  | Cable
300 | 15 | X12 | 107 | 1 | W89 | 1 | + |  | Cable | LST-20B.2 Lye Level Fas/Lye Separator 20B
301 | 15 | X12 | 108 | 2 | W89 | 2 | - |  | Cable
302 | 15 | X12 | 109 | 1 | W90 | 1 | + | Analyser | Cable | OJ-67.1 O2/H H2 Analyser
303 | 15 | X12 | 110 | 2 | W90 | 2 | - |  | Cable
304 | 15 | X12 | 111 | 3 | W90 | 3 | + |  | Cable
305 | 15 | X12 | 112 | 4 | W90 | 4 | - |  | Cable
306 | 16 | X12 | 113 | 1 | W91 | 1 | 1 | Analyser | Cable | MT-68A.1 DY-75 H2O In O2 Analyser A
307 | 16 | X12 | 114 | 2 | w91 | 2 | 2 |  | Cable
308 | 16 | X12 | 115 | 3 | W91 | 3 | 3 |  | Cable
309 | 16 | X12 | 116 | 1 | w92 | 1 | + | Bypass Valve | Cable | I/PN-13.3 I/P Converter Bypass Valve
310 | 16 | X12 | 117 | 2 | w92 | 2 | - |  | Cable
311 | 16 | X12 | 118 | 1 | w93 | 1 | 1 | Analyser | Cable | MT-68B.1 DY-75 H2O In O2 Analyser B
312 | 16 | X12 | 119 | 2 | w93 | 2 | 2 |  | Cable
313 | 16 | X12 | 120 | 3 | w93 | 3 | 3 |  | Cable
314 | 16 | X12 | 121 | 1 | w94 | 1 | +2 | Analyser | Cable | OT-27A.1 Gas Analyser H2 In O2 Electrolyser A
315 | 16 | X12 | 122 | 2 | w94 | 2 | -3 |  | Cable
316 | 16 | X12 | 123 | 3 | w94 | 3 | +1 |  | Cable
317 | 16 | X12 | 124 | 4 | w94 | 4 | -4 |  | Cable
318 | 16 | X12 | 125 | 1 | w95 | 1 | +2 | Analyser | Cable | OT-27B.1 Gas Analyser H2 In O2 Electrolyser B
319 | 16 | X12 | 126 | 2 | w95 | 2 | -3 |  | Cable
320 | 16 | X12 | 127 | 3 | w95 | 3 | +1 |  | Cable
321 | 16 | X12 | 128 | 4 | w95 | 4 | -4 |  | Cable
322 | 16 | X12 | 129 | 1 | w96 | 1 | +5 | Dryer A | Cable | TT-64A.7 PT100 Dryer 64A
323 | 16 | X12 | 130 | 2 | w96 | 2 | -6 |  | Cable
324 | 16 | X12 | 131 | 1 | w97 | 1 | +5 | Dryer B | Cable | TT-64B.7 PT100 Dryer 64B
325 | 16 | X12 | 132 | 2 | w97 | 2 | -6 |  | Cable
S/N | PAGE | CUBICLE | CUBICLE PIN | DEVICE NAME | PLC | PLC PIN | DEVICE TYPE | MACHINE |  | CONNECTION | DESCRIPTION | COMMENTS
109 | 52 | PLCX1 | 1 |  | X00 | 1 |  | TRIP AND ALAM |  |  | CUSTOMER REC. TO ZERO
110 | 52 | PLCX1 | 20 |  | X01 | 20 |  | TRIP AND ALAM |  |  | FIRE DETECTION TRIP
105 | 51 | PLCX1 | 2 |  | X02 | 2 |  | EMERGENCY SWITCH |  |  | HS 1.2A EMERGENCY SWITCH
106 | 51 | PLCX1 | 21 |  | X03 | 21 |  | EMERGENCY SWITCH |  |  | HS 1.2B EMERGENCY SWITCH
107 | 51 | PLCX1 | 3 |  | X04 | 3 |  | EMERGENCY SWITCH |  |  | HS 1.2C EMERGENCY SWITCH
19 | 19 | PLCX1 | 22 | K2A | X05 | 22 |  |  | Diff Current Relay |  | MAIN BREAKER
80 | 44 | PLCX1 | 23 |  | X06 | 23 |  | RECTIFIER B |  |  | COMMON ALARM RECTIFIER B
79 | 44 | PLCX1 | 4 |  | X07 | 4 |  | RECTIFIER B |  |  | COMMON ALARM RECTIFIER B
61 | 40 | PLCX1 | 5 |  | X08 | 5 |  | LYE PUMP 30AB |  |  | LYE PUMP 30AB START/STOP
62 | 40 | PLCX1 | 24 |  | X09 | 24 |  | LYE PUMP 30AB |  |  | LYE PUMP 30AB START/STOP
63 | 40 | PLCX1 | 6 | FR30AB | X0A | 6 |  | LYE PUMP 30AB |  |  | LYE PUMP 30AB START/STOP
88 | 47 | PLCX1 | 25 |  | X0B | 25 |  | RECTIFIER A |  |  | RECTIFIER A COMMON ALARM
89 | 47 | PLCX1 | 26 |  | X0D | 26 |  | RECTIFIER A |  |  | RECTIFIER A ON
153 | 65 | PLCX1 | 9 | U2 | X10 | 9 |  | PRESSURE H2 | SWITCH | FXAC2-2 | PRESS. SWITCH PSL-101.3 PRESSURE H2 INLET
184 | 70 | PLCX1 | 28 | U17 | X11 | 28 |  | DRYER 64B | SWITCH | FXAC 2-17 | PRESSURE SWITCH PSH 64B.1 OUTLET PRESSURE TOWER A DRYER 64B
64 | 40 | PLCX1 | 10 | KM30AB | X12 | 10 |  | LYE PUMP 30AB |  |  | LYE PUMP 30AB START/STOP
56 | 39 | PLCX1 | 29 |  | X13 | 29 |  | LYE PUMP 30AA |  |  | LYE PUMP 30AA ON/OFF
57 | 39 | PLCX1 | 11 |  | X14 | 11 |  | LYE PUMP 30AA |  |  | LYE PUMP 30AA ON/OFF
58 | 39 | PLCX1 | 30 | FR30AA | X15 | 30 |  | LYE PUMP 30AA |  |  | LYE PUMP 30AA ON/OFF
167 | 67 | PLCX1 | 12 | U9 | X16 | 12 |  | LYE/GAS SEPARATOR | SWITCH | FXAC 2-9 | LEVEL SWITCH LST 20A.2 LOW LOW LEVEL 01 LYE/GAS SEPARATOR
179 | 69 | PLCX1 | 31 | U15 | X17 | 31 |  | GAS/LYE SEPARATOR | SWITCH | FXAC 2-15 | TEMP. SWITCH TIS-10A.2 LYE TEMP.ELECT.A GAS/LYE SEPARATOR
189 | 71 | PLCX1 | 31 | U20 | X18 | 31 |  | COMPRESSOR 81B | SWITCH | FXAC 2-20 | PRESSURE SWITCH PSH-81B.12 DISCHARGE PRESSURE COMPRESSOR 81B
46 | 37 | PLCX1 | 32 | HS 15A.1 | X19 | 32 |  | SCRUBBER 15A |  |  | SCRUBBER 15A ON/OFF
47 | 37 | PLCX1 | 14 | HS 15A.1 | X1A | 14 |  | SCRUBBER 15A |  |  | SCRUBBER 15A ON/OFF
48 | 37 | PLCX1 | 33 | FR 15A | X1B | 33 |  | SCRUBBER 15A |  |  | SCRUBBER 15A ON/OFF
66 | 41 | PLCX1 | 15 |  | X1C | 15 |  | LYE PUMP 30BA |  |  | LYE PUMP 30BA START/STOP
169 | 68 | PLCX1 | 34 | U10 | X1D | 34 |  | SCRUBBER | SWITCH | FXAC 2-10 | LEVEL SWITCH LSL-14.2 LEVEL LOW FEED WATER SCRUBBER ITEM 14
168 | 67 | PLCX1 | 16 | U9 | X1E | 16 |  | SCRUBBER | SWITCH | FXAC 2-9 | LEVEL SWITCH LSLL-14.2 LEVEL LOW LOW FEED WATER SCRUBBER
177 | 69 | PLCX1 | 35 | U14 | X1F | 35 |  | GAS HOLDER | SWITCH | FXAC 2-14 | LEVEL SWITCH LSL-13.2 LOW LEVEL GASHOLDER
163 | 67 | PLCX1 | 7 | U7 | XOC | 7 |  | ELECTROLYSER B | SWITCH | FXAC 2-7 | FLOW SWITCH FIS-30B.2 LYE CIRC. LOW ELECTROLYSER B
152 | 65 | PLCX1 | 27 | U1 | XOF | 27 |  | AIR INLET | SWITCH | FXAC 2-1 | PRESS. SWITCH PSL-101.2 PRESSURE INSTRUMENT AIR INLET
151 | 65 | PLCX1 | 8 | U1 | XOE | 8 |  | WATER MAIN INLET | SWITCH | FXAC 2-1 | PRESS. SWITCH PSL-101.1 COOLING WATER MAIN INLET
94 | 49 | PLCX2 | 1 |  | X20 | 1 |  | COMPRESSOR A |  |  | COMPRESSOR A START/STOP
95 | 49 | PLCX2 | 20 |  | X21 | 20 |  | COMPRESSOR A |  |  | COMPRESSOR A START/STOP
97 | 49 | PLCX2 | 2 | FR81A | X22 | 2 |  | COMPRESSOR A |  |  | COMPRSSOR A FAULT/RUNNING
156 | 65 | PLCX2 | 21 | U3 | X23 | 21 |  | DISCHARGE PRESSURE | SWITCH | FXAC2-3 | PRESSURE SWITCH PSH-81A.12 DISCHARGE PRESSURE COMPRESSOR 81A
190 | 71 | PLCX2 | 3 | U20 | X24 | 3 |  |  | SWITCH | FXAC 2-20 |  | SPARE
191 | 71 | PLCX2 | 22 | U21 | X25 | 22 |  | COMPRESSOR 81B | SWITCH | FXAC 2-21 | TEMP. SWITCH TSH-81B.13 DISCHARGE TEMP. COMPRESSOR 81B
154 | 65 | PLCX2 | 4 | U2 | X26 | 4 |  |  | SWITCH | FXAC 2-2 |  | SPARE
155 | 65 | PLCX2 | 23 | U3 | X27 | 23 |  | CONDENSATE TANK | SWITCH | FXAC 2-3 | PRESS. SWITCH PSH-B1A.20 PRESSURE CONDENSATE TANK COMPRESSOR 81.A
192 | 71 | PLCX2 | 5 | U21 | X28 | 5 |  | COMPRESSOR 81B | SWITCH | FXAC 2-21 | LEVEL SWITCH LSLL-81B.14 CONDENSATE LEVEL LOW LOW COMPRESSOR 81.B
194 | 72 | PLCX2 | 24 | U22 | X29 | 24 |  | COMPRESSOR 81B | SWITCH | FXAC 2-22 | LEVEL SWITCH LSLH 81B.16 CONDENSE LEVEL HIGH COMPRESSOR 81B
193 | 72 | PLCX2 | 6 | U22 | X2A | 6 |  | COMPRESSOR 81B | SWITCH | FXAC 2-22 | LEVEL SWITCH LSL-81B.15 CONDENSATE LEVEL OW COMPRESSOR 81.B
67 | 41 | PLCX2 | 25 |  | X2B | 25 |  | LYE PUMP 30BA |  |  | LYE PUMP 30BA START/STOP
68 | 41 | PLCX2 | 7 | FR30BA | X2C | 7 |  | LYE PUMP 30BA |  |  | LYE PUMP 30BA START/STOP
101 | 50 | PLCX2 | 26 |  | X2D | 26 |  | COMPRESSOR 81B |  |  | COMPRESSOR START/ STOP
103 | 50 | PLCX2 | 8 | FR81B | X2E | 8 |  | COMPRESSOR 81B |  |  | COMPRESSOR 81B FAULT
69 | 41 | PLCX2 | 27 | KM30BA | X2F | 27 |  | LYE PUMP 30BA |  |  | LYE PUMP 30BA START/STOP
36 | 34 | PLCX2 | 34 | HS64A.1 | X30 | 34 |  | DRYER 64A |  |  | DRYER START/STOP/ IN OPERATION
73 | 42 | PLCX2 | 9 | FR30BB | X30 | 9 |  | LYE PUMP 30BB |  |  | LYE PUMP 30BB START/STOP
74 | 42 | PLCX2 | 28 | KM30BB | X31 | 28 |  | LYE PUMP 30BB |  |  | LYE PUMP 30BB START/STOP
71 | 42 | PLCX2 | 10 |  | X32 | 10 |  | LYE PUMP 30BB |  |  | LYE PUMP 30BB START/STOP
72 | 42 | PLCX2 | 29 |  | X33 | 29 |  | LYE PUMP 30BB |  |  | LYE PUMP 30BB START/STOP
96 | 49 | PLCX2 | 11 |  | X34 | 11 |  | COMPRESSOR A |  |  | COMPRESSOR A EMERGENCY SWITCH
102 | 50 | PLCX2 | 30 |  | X35 | 30 |  | COMPRESSOR 81B |  |  | COMPRESSOR 81B EMERGENCY SWITCH
51 | 38 | PLCX2 | 12 |  | X36 | 12 |  | SCRUBBER 15B |  |  | SCRUBBER 15B ON/OFF
52 | 38 | PLCX2 | 31 |  | X37 | 31 |  | SCRUBBER 15B |  |  | SCRUBBER 15B ON/OFF
43 | 36 | PLCX2 | 13 | HS60.5 | X38 | 13 |  | DEOXIDISER |  |  | DEOXIDISER HEATER ON/OFF
160 | 66 | PLCX2 | 33 | U5 | X38 | 33 |  |  | SWITCH | FXAC 2-5 |  | SPARE
158 | 66 | PLCX2 | 32 | U4 | X39 | 32 |  |  | SWITCH | FXAC 2-4 |  | SPARE
159 | 66 | PLCX2 | 14 | U5 | X3A | 14 |  |  | SWITCH | FXAC 2-5 |  | SPARE
161 | 66 | PLCX2 | 15 | U6 | X3C | 15 |  | DEOXIDISER | SWITCH | FXAC 2-6 | TEMP. SWITCH TSHH - 60.3 OUTLET TEMP HIGH HIGH DEOXIDISER
178 | 69 | PLCX2 | 16 | U14 | X3E | 16 |  | ELECTROLYSER | SWITCH | FXAC 2-14 | FLOW SWITCH F1SL-30A.2 LYE CIRCULATION LOW ELECTROLYZER SYST. ES1
180 | 69 | PLCX2 | 35 | U15 | X3F | 35 |  | DRYER 64 A | SWITCH | FXAC 2-15 | TEMP. SWITCH TS-64A.6 HEATER TEMP DRYER 64 A
41 | 36 | PLCX2 | 33 | K60 | Y38 | 33 |  | DEOXIDISER | SOLENOID |  | DEOXIDISER HEATER ON/OFF
182 | 70 | PLCX3 | 21 | U16 | X4# | 21 |  | DRYER 64A | SWITCH | FXAC 2-16 | PRESSURE SWITCH PSH64A.2 OUTLET PRESSURE TOWER B DRYER 64A
44 | 36 | PLCX3 | 26 | KM60 | X40 | 13 |  | DEOXIDISER |  |  | DEOXIDISER HEATER ON/OFF
197 | 72 | PLCX3 | 1 | U24 | X40 | 1 |  | DRYER 64A | SWITCH | FXAC 2-24 | PRESSURE SWITCH PSL. 64A.1 OUTLET PRESSURE TOWER A DRYER 64A
198 | 72 | PLCX3 | 20 | U24 | X41 | 20 |  | DRYER 64A | SWITCH | FXAC 2-24 | PRESSURE SWITCH PSH 64A.1 OUTLET PRESSURE TOWER A DRYER 64A
181 | 70 | PLCX3 | 2 | U16 | X42 | 2 |  | DRYER 64A | SWITCH | FXAC 2-16 | PRESSURE SWITCH PSL-64A.2 OUTLET PRESSURE TOWER B DRYER 64A
183 | 70 | PLCX3 | 3 | U17 | X44 | 3 |  | DRYER 64B | SWITCH | FXAC 2-17 | PRESSURE SWITCH PSL 64B.1 OUTLET PRESSURE TOWER A DRYER 64B
100 | 50 | PLCX3 | 22 |  | X45 | 22 |  | COMPRESSOR 81B |  |  | COMPRESSOR START/ STOP
195 | 72 | PLCX3 | 4 | U23 | X46 | 4 |  | COMPRESSOR 81B | SWITCH | FXAC 2-23 | LEVEL SWITCH LSHH 81B.17 CONDENSE LEVEL HIGH HIGH COMPRESSOR 81B
39 | 35 | PLCX3 | 23 | HS64B.1 | X47 | 23 |  | DRYER 64B |  |  | DRYER START/STOP/ IN OPERATION
108 | 51 | PLCX3 | 5 |  | X48 | 5 |  | EMERGENCY SWITCH |  |  | HS 1.2D EMERGENCY SWITCH
145 | 63 | PLCX3 | 5 | S27A.1 | X48 | 5
59 | 39 | PLCX3 | 24 | KM30AA | X49 | 24 |  | LYE PUMP 30AA |  |  | LYE PUMP 30AA ON/OFF
49 | 37 | PLCX3 | 6 | KM15A | X4A | 6 |  | SCRUBBER 15A |  |  | SCRUBBER 15A ON/OFF
98 | 49 | PLCX3 | 25 | KM81A | X4B | 25 |  | COMPRESSOR A |  |  | COMPRSSOR A FAULT/RUNNING
104 | 50 | PLCX3 | 7 | KM81B | X4C | 7 |  | COMPRESSOR 81B |  |  | COMPRESSOR 81B RUNNING
37 | 34 | PLCX3 | 8 | KM64A | X4E | 8 |  | DRYER 64A |  |  | DRYER START/STOP/ IN OPERATION
196 | 72 | PLCX3 | 27 | U23 | X4F | 27 |  |  | SWITCH | FXAC 2-23 |  | SPARE
40 | 35 | PLCX3 | 9 | KN64B | X50 | 9 |  | DRYER 64B |  |  | DRYER START/STOP/ IN OPERATION
175 | 69 | PLCX3 | 34 | U13 | X50 | 34 |  | COMPRESSOR A | SWITCH | FXAC 2-13 | LEVEL SWITCH LSHH-81A.17 CONDENSATE LEVEL HIGH HIGH HP COMPRESSOR A
188 | 71 | PLCX3 | 10 | U19 | X52 | 10 |  | COMPRESSOR 81B | SWITCH | FXAC 2-19 | PRESSURE SWITCH PSH-81B.20 PRESSURE CONDENSATE TANK COMPRESSOR 81B
157 | 66 | PLCX3 | 29 | U4 | X53 | 29 |  |  | SWITCH | FXAC 2-4 |  | SPARE
162 | 66 | PLCX3 | 11 | U6 | X54 | 11 |  | ELECTROLYSER B | SWITCH | FXAC 2-6 | LEVEL SWITCH LST 20B.2 LOW LOW LEVEL ELECTROLYSER B
164 | 67 | PLCX3 | 30 | U7 | X55 | 30 |  | DRYER 64B | SWITCH | FXAC 2-7 | FLOW SWITCH FSL-64B.5 LOW LEVEL DRYER 64B
165 | 67 | PLCX3 | 12 | U8 | X56 | 12 |  | DRYER 64A | SWITCH | FXAC 2-8 | FLOW SWITCH FSL-64B.5 LOW LEVEL DRYER 64A
166 | 67 | PLCX3 | 31 | U8 | X57 | 31 |  | GAS/LYE SEPARATOR | SWITCH | FXAC 2-8 | TEMP. SWITCH TIS-10B.2 LYE TEMP. ELECT.B GAS/LYE SEPARATOR B
170 | 68 | PLCX3 | 13 | U10 | X58 | 14 |  | SCRUBBER | SWITCH | FXAC 2-10 | LEVEL SWITCH LSLH-14.2 LEVEL HIGH FEED WATER SCRUBBER ITEM 14
171 | 68 | PLCX3 | 32 | U11 | X59 | 32 |  | COMPRESSOR A | SWITCH | FXAC 2-11 | TEMP. SWITCH TSH-81A.13 DISCHARGE TEMPERATURE H2 COMPRESSOR A
172 | 68 | PLCX3 | 14 | U11 | X5A | 14 |  | COMPRESSOR A | SWITCH | FXAC 2-11 | LEVEL SWITCH LSLL-81A CONDENSATE LEVEL LOW LOE RECIEV. TNK. COMPR.A
173 | 68 | PLCX3 | 33 | U12 | X5B | 33 |  | COMPRESSOR A | SWITCH | FXAC 2-12 | LEVEL SWITCH LSL-81A.15 CONDENSATE LEVEL LOW RECIEV. TNK. HP.COMPR.A
174 | 68 | PLCX3 | 15 | U12 | X5C | 15 |  | COMPRESSOR A | SWITCH | FXAC 2-12 | LEVL SWITCH LSLH-81A.16 CONDENSATE LEVEL HIGH RECIEVER TANK HP.COMPRESSOR A
176 | 69 | PLCX3 | 16 | U13 | X5E | 16 |  | DRYER 64B | SWITCH | FXAC 2-13 | TEMP. SWITCH TS-64.6 HEATER TEMP DRYER 64B
54 | 38 | PLCX4 | 5 | KM15B | X018 | 5 |  | SCRUBBER 15B |  |  | SCRUBBER 15B ON/OFF
185 | 70 | PLCX4 | 20 | U18 | X101 | 20 |  | DRYER 64B | SWITCH | FXAC 2-18 | PRESSURE SWITCH PSL-64B.2 OUTLET PRESSURE TOWER B DRYER 64B
186 | 70 | PLCX4 | 2 | U18 | X102 | 2 |  | DRYER 64B | SWITCH | FXAC 2-18 | PRESSURE SWITCH PSH 64B.2 OUTLET PRESSURE TOWERB DRYER 64B
187 | 71 | PLCX4 | 21 | U19 | X103 | 21 |  |  | SWITCH | FXAC 2-19 |  | SPARE
113 | 53 | PLCX4 | 3 |  | X104 | 3 |  | H2 IN AIR |  |  | H2 IN AIR
115 | 53 | PLCX4 | 4 |  | X106 | 4 |  | H2 IN AIR |  |  | H2 IN AIR
53 | 38 | PLCX4 | 23 | FR 15B | X107 | 23 |  | SCRUBBER 15B |  |  | SCRUBBER 15B ON/OFF
34 | 33 | PLCX4 | 6 |  | X10A | 6 |  | WATER PRIFICATION |  |  | EXISTING DEMINERAKISED WATER PLANT
114 | 53 | PLCX4 | 22 |  | X105 | 22 |  | H2 IN AIR |  |  | H2 IN AIR
65 | 41 | PLCY1 | 11 | K20BA | X74 | 11 |  | LYE PUMP 30BA | SOLENOID | FXAC 1-07 | LYE PUMP 30BA START/STOP
111 | 52 | PLCY1 | 1 | K01 | Y60 | 1 |  | TRIP AND ALAM | SOLENOID |  | COMMON YELOW ALARM
112 | 52 | PLCY1 | 20 | K02 | Y61 | 20 |  | TRIP AND ALAM | SOLENOID |  | COMMON RED ALARM
90 | 48 | PLCY1 | 3 | K11A | Y64 | 3 |  | RECTIFIER A | SOLENOID |  | RECTIFIER A RUN/BLOCK
55 | 39 | PLCY1 | 4 | K20AA | Y66 | 4 |  | LYE PUMP 30AA | SOLENOID | FXAC1-01 | LYE PUMP 30AA ON/OFF
116 | 54 | PLCY1 | 23 | K508 | Y67 | 23 |  | ELECTROLYSER B | Solenoid | FXAC-1-14 | FEED WATER SUPPLY LYE SYSTEM (CONTROL VALVE FW-111B-1) ELECTROLYSER B
81 | 45 | PLCY1 | 23 | K11B | Y68 | 23 |  | RECTIFIER B | SOLENOID |  | RECTIFIER B RUN/BLOCK
117 | 54 | PLCY1 | 24 | K23 | Y69 | 24 |  | SCRUBBER | Solenoid | FXAC-1-13 | FEED WATER SUPPLY SCRUBBER
93 | 49 | PLCY1 | 6 | K30A | Y6A | 6 |  | COMPRESSOR A | SOLENOID |  | COMPRESSOR A START/STOP
135 | 60 | PLCY1 | 25 | K31B | Y6B | 25 |  | COMPRESOR 81B VALVE | Solenoid | FXAC-1-21 | DRAINING 1'ST STAGE COMPR.81B VALVE 81B-V13
136 | 60 | PLCY1 | 7 | K32B | Y6C | 7 |  | COMPRESSOR 81B VALVE | Solenoid | FXAC1-22 | DRAINING 2'ND STAGE COMPR. 81B VALVE 81B-V14
137 | 60 | PLCY1 | 26 | K33B | Y6D | 26 |  | COMPRESSOR 81B VALVE | Solenoid | FXAC-1-23 | DRAINING 3'RD STAGE SEP. COMPR.81B VALVE 81B-V15
139 | 61 | PLCY1 | 8 | K35B | Y6E | 8 |  | COMPRESSOR 81B VALVE | Solenoid | FXAC-1-25 | DRAINING AFTER FILTER COMPR.81B VALVE 81B-V41
140 | 61 | PLCY1 | 27 | K36B | Y6F | 27 |  | COMPRESSOR 81B VALVE | Solenoid | FXAC-1-26 | DRAINING COND. POTCOMP. 81B VALVE 81B-V31
99 | 50 | PLCY1 | 9 | K30B | Y70 | 9 |  | COMPRESSOR 81B | SOLENOID | FXAC 1-9 | COMPRESSOR START/ STOP
138 | 61 | PLCY1 | 28 | K34B | Y71 | 28 |  | COMPRESSOR 81B VALVE | Solenoid | FXAC-1-24 | DRAINING 4'TH STAGE COMP.81B VALVE 81B-V16
60 | 40 | PLCY1 | 29 | K20AB | Y73 | 29 |  | LYE PUMP 30AB | SOLENOID | FXAC 1-02 | LYE PUMP 30AB START/STOP
38 | 35 | PLCY1 | 30 | K41B | Y75 | 30 |  | DRYER 64B | SOLENOID | FXAC -1-11 | DRYER START/STOP/ IN OPERATION
42 | 36 | PLCY1 | 12 | K40 | Y76 | 12 |  | DEOXIDISER | SOLENOID | FXAC -1-05 | DEOXIDISER HEATER ON/OFF
35 | 34 | PLCY1 | 31 | K41A | Y77 | 31 |  | DRYER 64A | SOLENOID | FXAC 1-06 | DRYER START/STOP/ IN OPERATION
125 | 57 | PLCY1 | 13 | K31A | Y78 | 13 |  | COMPRESOR 81A VALVE | Solenoid | FXAC-1-15 | DRAINAGE 1'ST STAGE COMP. 81A VALVE 81A -V13
126 | 57 | PLCY1 | 32 | K32A | Y79 | 32 |  | COMPRESOR 81A VALVE | Solenoid | FXAC-1-16 | DRAINAGE 2'ND STAGE COMP. 81A VALVE 81A -V14
141 | 62 | PLCY1 | 14 | K44B | Y7A | 14 |  | DRYER 64B | Solenoid | FXAC-1-35 | VENTILATION TO ATMOSPHERE DRYER 64B
118 | 54 | PLCY1 | 33 | K21A | Y7B | 33 |  | ELECTROLYSER B | Solenoid | FXAC-1-27 | FEED WATER SUPPLY LYE SYSTEM (CONTROL VALVE FW-111B-2) ELECTROLYSER B
127 | 57 | PLCY1 | 15 | K33A | Y7C | 15 |  | COMPRESOR 81A VALVE | Solenoid | FXAC-1-17 | DRAINAGE 3'RD STAGE COMP. SEP. COMPR. 81A VALVE 81A-V15 | XW (100) 24Vdc
128 | 58 | PLCY1 | 34 | K34A | Y7D | 34 |  | COMPRESOR 81A VALVE | Solenoid | FXAC-1-18 | DRAINAGE 4TH STAGE COMPR. 81A VALVE 81A-V16
129 | 58 | PLCY1 | 16 | K35A | Y7E | 16 |  | COMPRESOR 81A VALVE | Solenoid | FXAC-1-19 | DRAINAGE AFETR FILTER COMPR.81A VALVE 81A-V41
130 | 58 | PLCY1 | 35 | K36A | Y7F | 35 |  | COMPRESOR 81A VALVE | Solenoid | FXAC-1-20 | DRAINING COND. POTCOMP. 81A VALVE 81A-V31
45 | 37 | PLCY2 | 26 | K22A | Y120 | 26 |  | SCRUBBER 15A | SOLENOID | FXAC 1-04 | SCRUBBER 15A ON/OFF
131 | 59 | PLCY2 | 1 | K44A | Y120 | 1 |  | DRYER | Solenoid | FXAC-1-28 | VENTILATION TO ATMOSPHERE DRYER 64A
132 | 59 | PLCY2 | 20 | K45A | Y121 | 20 |  | DRYER 64A | Solenoid | FXAC-1-29 | DRAIN DRYER 64A
119 | 55 | PLCY2 | 2 | K48A | Y123 | 3 |  | DRYER 64A | Solenoid | FXAC-1-32 | LIMIT VALVE TOWER A DRYER 64A
134 | 59 | PLCY2 | 21 | K47A | Y123 | 21 |  | DRYER 64A | Solenoid | FXAC-1-31 | TOWER B IN OPERATION DRYER 64A
120 | 55 | PLCY2 | 22 | K49A | Y125 | 22 |  | DRYER 64A | Solenoid | FXAC-1-33 | LIMIT VALVE TOWER B DRYER 64A
121 | 55 | PLCY2 | 4 | K51A | Y126 | 4 |  | DRYER 64A | Solenoid | FXAC-1-34 | DISCHARGE VALVE DRYER 64A
142 | 62 | PLCY2 | 23 | K45B | Y127 | 23 |  | DRYER 64B | Solenoid | FXAC-1-36 | DRAIN DRYER 64B
143 | 62 | PLCY2 | 5 | K46B | Y128 | 5 |  | DRYER 64B | Solenoid | FXAC-1-37 | TOWER A IN OPERATION DRYER 64B
144 | 62 | PLCY2 | 24 | K47B | Y129 | 24 |  | DRYER 64B | Solenoid | FXAC-1-38 | TOWER B IN OPERATION DRYER 64B
123 | 56 | PLCY2 | 25 | K49B | Y12B | 25 |  | DRYER 64B | Solenoid | FXAC-1-40 | LIMIT VALVE TOWER B DRYER 64B
124 | 56 | PLCY2 | 7 | K51B | Y12C | 7 |  | DRYER 64B | Solenoid | FXAC-1-41 | DISCHARGE VALVE DRYER 64B
50 | 38 | PLCY2 | 8 | K22B | Y12E | 8 |  | SCRUBBER 15B | SOLENOID | FXAX 1-10 | SCRUBBER 15B ON/OFF
70 | 42 | PLCY2 | 27 | K20BB | Y12F | 27 |  | LYE PUMP 30BB | SOLENOID |  | LYE PUMP 30BB START/STOP
33 | 33 | PLCY2 | 9 |  | Y130 | 9 |  | WATER PRIFICATION |  |  | CONTROL SUPPLY VOLTAGE/ REVERSE OSMOSIS PLANT
122 | 56 | PLCY2 | 6 | K48B | Y12A | 6 |  | DRYER 64B | Solenoid | FXAC-1-39 | LIMIT VALVE TOWER A DRYER 64B
133 | 59 | PLCY2 | 2 | K44A | Y122 | 2 |  | DRYER 64A | Solenoid | FXAC-1-30 | TOWER A IN OPERATION DRYER 64A
148 | 64 | PLCX3 | 28 | S27B.1 | X51 | 28 |  | H2 IN O2 HH | Switch
82 | 45 |  |  |  | A0 1-3 | 7 |  | RECTIFIER B | GALVANIC OUT |  | RECTIFIER B CONTROL
83 | 45 |  |  |  | A0 1-3 | 8 |  | RECTIFIER B | GALVANIC OUT |  | RECTIFIER B CONTROL
215 | 76 |  |  | ZO3 | AI 1-1 | 1 |  |  | GALVANIC IN
216 | 76 |  |  | ZO4 | AI 1-2 | 2 |  |  | GALVANIC IN
217 | 76 |  |  | ZO4 | AI 1-2 | 4 |  |  | GALVANIC IN
220 | 77 |  |  | Z14 | AI 1-3 | 7 |  |  | GALVANIC IN
221 | 77 |  |  | Z14 | AI 1-3 | 9 |  |  | GALVANIC IN
201 | 73 |  |  | ZO6 | AI 1-4 | 6 |  |  | GALVANIC IN
202 | 73 |  |  | ZO6 | AI 1-4 | 10 |  |  | GALVANIC IN
146 | 63 |  |  |  | AI 1-5 | 11 |  |  | GALVANIC IN
147 | 63 |  |  |  | AI 1-5 | 13 |  |  | GALVANIC IN
84 | 46 |  |  |  | AI 1-6 | 12 |  | RECTIFIER | GALVANIC IN |  | RECTIFIER A VOLTAGE
85 | 46 |  |  |  | AI 1-6 | 14 |  | RECTIFIER | GALVANIC IN |  | RECTIFIER A VOLTAGE
86 | 46 |  |  |  | AI 1-7 | 17 |  | RECTIFIER | GALVANIC IN |  | RECTIFIER A CURRENT OUTPUT
87 | 46 |  |  |  | AI 1-7 | 19 |  | RECTIFIER | GALVANIC IN |  | RECTIFIER A CURRENT OUTPUT
209 | 75 |  |  | ZO8 | AI 1-8 | 18 |  |  | GALVANIC IN
210 | 75 |  |  | ZO8 | AI 1-8 | 20 |  |  | GALVANIC IN
211 | 75 |  |  | ZO9 | AI 2-1 | 1 |  |  | GALVANIC IN
212 | 75 |  |  | ZO9 | AI 2-1 | 3 |  |  | GALVANIC IN
75 | 43 |  |  |  | AI 2-2 | 2 |  | RECTIFIER B | GALVANIC IN |  | RECTIFIER B
76 | 43 |  |  |  | AI 2-2 | 4 |  | RECTIFIER B | GALVANIC IN |  | RECTIFIER B
77 | 43 |  |  |  | AI 2-3 | 7 |  | RECTIFIER B | GALVANIC IN |  | RECTIFIER B
78 | 43 |  |  |  | AI 2-3 | 9 |  | RECTIFIER B | GALVANIC IN |  | RECTIFIER B
149 | 64 |  |  |  | AI 2-5 | 11 |  |  | GALVANIC IN
150 | 64 |  |  |  | AI 2-5 | 15 |  |  | GALVANIC IN
213 | 75 |  |  | Z12 | AI 2-6 | 12 |  |  | GALVANIC IN
214 | 75 |  |  | Z12 | AI 2-6 | 14 |  |  | GALVANIC IN
203 | 73 |  |  | Z11 | AI 2-7 | 17 |  |  | GALVANIC IN
204 | 73 |  |  | Z11 | AI 2-7 | 19 |  |  | GALVANIC IN
218 | 77 |  |  | Z13 | AI 2-8 | 18 |  |  | GALVANIC IN
219 | 77 |  |  | Z13 | AI 2-8 | 20 |  |  | GALVANIC IN
205 | 74 |  |  | ZO6 | AI 3-2 | 2 |  |  | GALVANIC IN
206 | 74 |  |  | ZO6 | AI 3-2 | 4 |  |  | GALVANIC IN
207 | 74 |  |  | Z11 | AI 3-3 | 7 |  |  | GALVANIC IN
208 | 74 |  |  | Z11 | AI 3-3 | 9 |  |  | GALVANIC IN
91 | 48 |  |  |  | AO 1 | 3 |  | RECTIFIER A | GALVANIC OUT |  | RECTIFIER A CONTROL
199 | 73 |  |  | GO1 | AO 1-2 | 5 |  |  | GALVANIC OUT
200 | 73 |  |  | GO1 | AO 1-2 | 6 |  |  | GALVANIC OUT
92 | 48 |  |  |  | AO1 | 0# |  | RECTIFIER A | GALVANIC OUT |  | RECTIFIER A CONTROL

## Sheet1
Alarm | Analog Input
Analyser | Analog Output
Byepass Valve | Solenoid
Compressor 81A | Switch
Compressor 81B
Cooling System
Deoxidiser
Drier 64A
Drier 64B
Electrolyser A
Electrolyser B
Emergency Stop
Gas Holder
H2 Pressure Bottles
Lye Pump
Lye Pump AA
Lye Pump AB
Lye Pump BA
Lye Pump BB
Lye Tank A
Lye Tank B
Rectifier A
Rectifier B
Scrubber
Scrubber Pump A
Scrubber Pump B
Water Purification